Facility Planning

# Initial Space Estimates (CEAS)

Version:  January 25, 2012

Maintenance:

References:

- Space Management Utilization Standards

- Definitions -- at back of this document, remove prior to printing

| Unit or Area: | Atmospheric Science | Contact Person: | Jim Waldram, Jeff Snider |
| --- | --- | --- | --- |
| SPACE NAME |
| Research Computer Laboratory. EN 6021 and EN 6021A |
| SPACE DESCRIPTION (one sentence) |
| Research Computer Laboratory. EN 6021 and EN 6021A |
| SPACE FUNCTION: Describe in detail the function of the space including the operations that will occur in the space. Include any special characteristics of the space such as natural light, acoustical separation, vibration control, humidity control, unusual power requirements, special finishes, etc. Space function or operation must support the mission and goals of the department, college and university. |
| Space for research computing, including a cluster, storage, servers, UNIX and PC-based processors, magnetic tape archive. As is discussed, operating these computer resources out of the centralized Information Technology Center (ITC) would be impractical and inefficient. |
| EXISTING OR NEW SPACE: Does this space exist presently? If so, then list room number(s). Otherwise, indicate new space. |
| Existing (room no.) or New: Existing (EN 6021 and EN 6021A, see attached drawing) Comments: This is cyberinfrastructure space requiring ongoing upgrades and maintenance. |
| IDEAL SPACE |
| What space is needed and the justification: Detail the space required for the function or operations above. Utilize the Space Management Utilization Standards for space planning guidelines. Do not use existing space as the template for space needs (unless this space works well). Identify actual space required. Identify planning standard utilized if Space Management Utilization Standards are not utilized. |
| Research performed by the Department of Atmospheric Science requires specialized computing support personnel and infrastructure. A recent review of ATSC’s computer services demonstrated that these services cannot be provided by the Information Technology Center, and also demonstrated that centralization of ATSC’s hardware at ITC would not be efficient. EN6021, cluster, disk storage, servers, UNIX and PC-based systems, storage Local space is required for: Multiple systems requiring local physical access for frequent system maintenance/enhancement/customization High bandwidth (10-40 Gbps) networking between local servers/services and clients Power required/supplied computer systems: 3 x 100A (3 phase) environmental control: 3 x 50A (3 phase) Power continuity (UPS) is required. 100 cubic feet of storage: four wall mounted shelves 8 x 1 ft. with 1 foot clearance freestanding cabinet 6 x 2 x 1.5 ft. with 3 ft. overhead clearance freestanding cabinet 6 x 3 x 1.5 ft. with 3 ft. overhead clearance freestanding cabinet 2.5 x 2 x 2.5 ft. with 3 ft. overhead clearance freestanding shelves 6.6 x 3 x 1 ft. (shelf clearance .5-1.5 ft) with 2.5 ft. overhead clearance 500 cubic feet of computer infrastructure/system rack space: one 12 x 4 x 6 ft. rack space with 2 ft. overhead clearance one 4 x 4 x 6.5 ft. rack space with 1.5 ft. overhead clearance 200+ cubic feet of space for expansion. 40 square ft. maintenance/console workspace: 4 x 2 x 3 ft. 4 x 3 x 3 ft. 6 x 3 x 3 ft. 150 cubic ft. of environmental control: 6 x 3 x 8 ft. EN6021A, magnetic tape archive and computer infrastructure spares 1200 cubic feet of storage tape storage: four 8 x 2 x 10 racks with 1 ft vertical separation one 4 x 2 x 10 rack with 1 ft. vertical separation one tape cabinet 4 x 2 x 8 with 2 ft. overhead clearance storage three tape shelves unit 3 x 2 x 10 with .5-2.5 ft. vertical separation two tape shelves unit 3 x 1 x 6 with 1-1.5 ft. vertical separation infrastructure spares: one cabinet 3 x 2 x 8 ft. with 2 ft. overhead storage one shelf unit 3 x 1.5 x 8 ft. with .5-1.5 ft. vertical separation and 2 ft. overhead Air-conditioning system: 10 ton unit controls 348 ASF with 13-18 °C airflow controlling room locations to 16-35 °C. Relative humidity is uncontrolled from 15-35 percent as sensed in unit. |
| Number of Occupants utilizing the space on a continuing basis by indicating the number of permanent workstations and/or offices below. Also indicate the number of occupants utilizing the space on a temporary basis such as students during advising or consultation or numbers of persons in a meeting. |
| Permanent: Temporary: 2 computer support staff Comments: |
| Furniture, Fixtures and Equipment: Provide brief description of the required furnishings, fixtures or equipment for each type of spaces such as office, workroom, classroom, conference room, etc. required to accommodate the function or operation above. |
| 6021 raised computer flooring environmental control computer hardware rack space 3 chairs 3 tables shelf and cabinet storage 6021A tape racks, cabinets and shelves hardware storage cabinets and shelves |
| SPACE PRIORITIES |
| If the ideal space is not available, what are the priorities for this unit? |
| High, medium, low: High Comments: |
| SPACE RELATIONSHIPS |
| Special access or location requirements: Deliveries that require ground floor access, or semi-trailer access, special foundations, etc. |
| Location adjacencies preferred: See Adjacency Format-use for defined unit grouping and separated unit group relationships in building. |
| Adjacent to office of Computer Support Specialist |
| Can unit be divided on separate floors or different areas of building? If so, describe the proper separations. |
| SKETCH OR GRAPHIC / Additional Information or requirements |